## Project Pipeline
Project ID | Project Name | Sub-Region | Primary Municipality | Communities Served | Project Type | Voltage | MW Added | MW Expandable To | Target ISD | Status / Phase | ESMP Page | Permitting Notes | Source Project / Initiative
5 | New East Eagle Substation #131 | EMA-North Metro Boston | Boston (East Boston) | East Boston, Chelsea | New Substation | 115/14kV | 75 |  | 2029 | EFSB Tentative Decision (late 2022) | 352 | EFSB 22-01 cert proceeding; underground transmission already installed | Mystic-East Eagle-Chelsea Reliability Project
18 | New Cambridge #8025 Substation | EMA-North Metro Boston | Cambridge (Kendall Sq) | East Cambridge, Putnam, Somerville | New Underground Substation | 115/14kV | 90 | 120 | 2029 | In construction (delayed from 2020 ISD) | 353 | Underground; 5 duct banks + 8 new 115kV lines; integrated w/ Boston Properties Kendall Center Blue Garage redevelopment | Greater Cambridge Energy Project
22 | New Hyde Park/Dorchester Substation | EMA-North Metro Boston | Boston (Hyde Park / Dorchester) | Hyde Park, Mattapan, Dorchester, Roslindale | New Substation | 115kV | 150 | 225 | 2029 | Proposed | 355 | Hyde Park #496 already at 100% capacity; BES NWA being developed for interim | Hyde Park-Dorchester Area Solution
1 | Somerville Substation #402 Expansion | EMA-North Metro Boston | Somerville | Somerville, Cambridge | Substation Expansion | 115kV | 75 |  | 2029 | Approved / In Progress | 356 | 3rd transformer + 2 distribution bus sections; driven by Boynton Yards & Union Square growth | Somerville Capacity Relief
13 | Alewife Substation Transformer Addition | EMA-North Metro Boston | Cambridge (North) | North Cambridge | Transformer Addition | 115kV | 75 |  | 2029 | Approved | 356 | Existing station with expansion capability | Alewife Capacity Expansion
27 | New South End Substation | EMA-North Metro Boston | Boston (South End) | South End, Roxbury, Dorchester | New Substation | 115kV | 150 | 225 | 2034 | Planned | 357 | Multiple 115kV underground transmission feeds required | Boston Substation Supply Initiative
30 | New Allston/Fenway/Brookline Substation | EMA-North Metro Boston | Brookline | Brookline, Fenway, LMA, Mission Hill, Jamaica Plain | New Substation | 115kV | 150 | 225 | 2034 | Planned | 358 | Located in Brookline between Allston & Fenway; underground 115kV feeds | Boston Substation Supply Initiative
26 | New Charlestown/Somerville Substation | EMA-North Metro Boston | Boston (Charlestown) / Somerville | Charlestown, North End, Somerville | New Substation | 115kV | 150 | 225 | 2034 | Planned | 359 | East or west of I-93/MBTA corridor; relieves Everett substation | Boston Substation Supply Initiative
32 | New Metro Boston Network Substation | EMA-North Metro Boston | Boston (Downtown) | Beacon Hill, West End, North End, Chinatown, Leather District | New Substation (Underground Network) | 115kV | 150 |  | 2034 | Planned | 360 | Serves the 6-substation downtown UG networked system; multiple 115kV UG feeds | Downtown Network Capacity
24 | Electric Ave Substation Transformer Addition | EMA-North Metro Boston | Boston (Brighton/Allston) | Brighton, Allston | Transformer Addition | 115kV |  |  | 2034 | Planned | 361 | Existing station with expansion capability | Boston Substation Supply Initiative
28 | Seafood Way Substation Transformer Addition | EMA-North Metro Boston | Boston (Seaport) | Seaport District | Transformer Addition | 115kV |  |  | 2034 | Planned | 361 | Existing station with expansion capability | Boston Substation Supply Initiative
19 | New Burlington Substation | EMA-North Metro West | Burlington | Burlington, Lexington, Woburn, Wilmington | New Substation + Transmission | 115/14kV | 75 |  | 2028 | In Permitting / Design | 371 | ~2 acres Eversource-owned land off Winn St; ~2.5 mi new OH transmission through Wilmington into Woburn; mobile transformer interim | Burlington-to-Woburn Supply Initiative
4 | Medway Substation Upgrade | EMA-North Metro West | Medway | Holliston, Medway, Millis, Norfolk | Transformer Replacement | 115/14kV | 20 |  | 2025 | Approved / In Progress | 372 | Replace 2x40 MVA with 62.5 MVA units + new HV breaker; 50 MVA mobile pre-staged Fall 2023 | Medway Capacity Solution
17 | Maynard Substation Upgrade | EMA-North Metro West | Maynard | Acton, Maynard | Substation Upgrade | 115kV | 20 |  | 2029 | Interim Operational Solution | 373 | Interim measure; long-term solution is North Acton (29) | Acton-Maynard Supply Initiative
25 | New Saxonville/Natick Substation | EMA-North Metro West | Natick / Framingham | Framingham, Natick, Holliston, Sherborn | New Substation | 115/14kV | 75 | 150 | 2031 | Planning Phase | 378 | Located near transmission ROW between Saxonville #278 and Framingham Ring #240 | Metro West Long-Range Plan
29 | New North Acton Substation | EMA-North Metro West | Acton | Acton, Maynard, Sudbury, Carlisle | New Substation | 115kV | 75 | 150 | 2033 | Planning Phase | 378 | Long-term replacement for Maynard interim | Acton-Maynard Long-Term Solution
33 | New Waltham Substation | EMA-North Metro West | Waltham | Waltham, Weston | New Substation | 115/14kV | 75 | 150 | 2034 | Planning Phase | 378 | Relieves North & West Waltham substations | Metro West Long-Range Plan
7 | New Falmouth Tap Substation | EMA-South | Falmouth | North Falmouth, Hatchville, South Bourne | Switching Station Rebuild + New Sub | 115/23kV | 75 |  | 2026 | In Design & Permitting | 391 | Rebuild existing #924 115kV switching station to breaker-and-a-half + new 115/23kV bulk distribution sub | Falmouth Tap Project
6 | 5th Submarine Cable to Martha's Vineyard | EMA-South | Falmouth / Tisbury | Martha's Vineyard | New Submarine Cable + Duct Bank | 23kV | 25 |  | 2024 | In Permitting & Design | 393 | 2.7 mi underground duct bank from Falmouth Station (Stephens Lane) → Surf Drive; 6.1 mi submarine across Vineyard Sound → East Chop (Eastville Ave) | Martha's Vineyard Reliability Project
22-47 | Marion-Fairhaven Group CIP (Wing Lane / Crystal Spring / Rochester) | EMA-South | Marion / Fairhaven / Rochester | Fairhaven, Acushnet, Mattapoisett, Rochester, Marion | Multi-Substation Upgrade (CIP) | 115kV |  |  | 2029 | DPU 22-47 Approved | 394 | Replace 6 existing transformers across Wing Lane #624, Crystal Spring #646, Rochester #745 (incl. new 37/50/62.5 MVA units) | DPU 22-47 Group Study CIP
EFT | East Freetown Group CIP (replaces New Bedford Group CIP) | EMA-South | East Freetown | New Bedford (north), East Freetown, Dartmouth, Acushnet, Rochester | New Substation (CIP) | 115kV |  |  | 2029 | Proposed CIP | 399 | New Substation #690; 69 MW DER + 12 MVA load transferred from Industrial Park #636 — RIGHT IN NEW BEDFORD AREA | East Freetown Group Study CIP
31 | New Dennis/Brewster Substation | EMA-South | Dennis / Brewster | Harwich, Dennis, Brewster, Chatham, Orleans | New Substation | 115/23kV | 75 |  | 2034 | Preliminary Stage | 397 | Lower Cape capacity solution | Lower Cape Capacity Project
2 | Clinton Substation Transformer Upgrade | WMA | Springfield | Springfield (3 hospitals + commercial) | Transformer Replacement | 115/13.8kV | 71 |  | 2024 | Internally Approved / In Progress | 413 | Replace 1 transformer + switchgears; serves critical hospital load | Clinton Capacity Upgrade
3 | Franconia Substation Upgrade | WMA | Springfield / Longmeadow | Springfield, Longmeadow | Transformer Replacement | 115/13.8kV | 5 |  | 2024 | Internally Approved | 413 | Replace 47 MVA transformer with 37.5/50/62.5 MVA | Franconia Capacity Upgrade
11 | Plainfield Substation Upgrade | WMA | Plainfield | Plainfield area | Transformer Replacement | 115kV | 29 |  | 2026 | Internally Approved | 413 | Replace 5 MVA with 37/50/62.5 MVA | Plainfield Capacity Upgrade
10 | Silver Substation Upgrade | WMA | Agawam | Agawam | Transformer Replacement (2x) | 115/14kV | 17 |  | 2026 | Approved / In Progress | 413 | Both transformers replaced with 37/50/62.5 MVA, one per year starting 2024 | Silver Capacity Upgrade
12 | Ludlow Substation Upgrade | WMA | Ludlow | Ludlow area | Substation Upgrade | 115kV | 37 |  | 2026 | Planning Phase | 414 | Single-transformer reliability fix; may add 2nd transformer or new distribution ROW | Ludlow Reliability Solution
16 | Partridge Substation Upgrade | WMA | Dalton / Lanesborough | Dalton, Lanesborough, New Ashford area | Substation Upgrade | 115kV | 32 |  | 2026 | Planning Phase | 414 | Single-transformer reliability fix | Partridge Reliability Solution
23 | New Worthington Substation | WMA | Worthington | Chester, Worthington, Plainfield, Blandford area | New Substation | 115/23kV | 75 |  | 2030 | Planning Phase | 422 | ~200 mi long feeders currently; needs new sub + transmission infrastructure | Chester-Worthington Reliability Project
WD-CIP | Whately-Deerfield Group CIP | WMA | Whately / Deerfield / Hatfield | Whately, Deerfield, Hatfield | New Substation (CIP) | 115/13.8kV |  |  | 2034 | Proposed CIP | 422 | Relieves Cumberland #22B, Montague 21C, Podick 18G, French King 21B, Shelburne 29R; enables ~189 MVA new DER beyond 86 MW Group Study | Whately-Deerfield Group Study CIP

## Hotspot Zones
Hotspot Zone | Sub-Region | Project Count | Total MW Added | Key Drivers
East Boston / Chelsea | EMA-North Metro Boston | 1 | 75 | Electrification, port growth, large step loads
Kendall Sq / Cambridge | EMA-North Metro Boston | 2 | 165 | Biotech / lab development, redevelopment
Hyde Park / Dorchester | EMA-North Metro Boston | 1 | 150 | Stations at >90% capacity, electrification
Somerville / Union Sq | EMA-North Metro Boston | 1 | 75 | Boynton Yards, Union Square growth
South End / Roxbury | EMA-North Metro Boston | 1 | 150 | Transportation electrification
Brookline / Fenway / LMA | EMA-North Metro Boston | 1 | 150 | Hospital + commercial growth
Charlestown / Everett | EMA-North Metro Boston | 1 | 150 | Relieves Everett, transportation electrification
Downtown Boston (Network) | EMA-North Metro Boston | 1 | 150 | UG network area capacity exhaustion
Brighton / Seaport | EMA-North Metro Boston | 2 |  | Existing station expansions
Burlington-Woburn corridor | EMA-North Metro West | 1 | 75 | Transformers >100% LTE rating
Medway-Holliston-Millis | EMA-North Metro West | 1 | 20 | Approaching LTE rating
Acton-Maynard | EMA-North Metro West | 2 | 95 | >95% capacity, growth
Framingham-Natick-Sherborn | EMA-North Metro West | 1 | 75 | Forecasted overloads
Waltham-Weston | EMA-North Metro West | 1 | 75 | N/W Waltham relief
Falmouth / Bourne / Cape | EMA-South | 1 | 75 | N-1 contingency events
Martha's Vineyard | EMA-South | 1 | 25 | Island reliability
Marion-Fairhaven-Mattapoisett-Rochester | EMA-South | 1 |  | DER queue at Wing Lane / Crystal Spring / Rochester
New Bedford / East Freetown / Dartmouth | EMA-South | 1 |  | Industrial Park #636 DER overload
Lower Cape (Harwich-Orleans) | EMA-South | 1 | 75 | Lower Cape capacity gap
Springfield / Longmeadow | WMA | 2 | 76 | Hospital + commercial growth
Agawam | WMA | 1 | 17 | Approaching 89% firm capacity
Plainfield-Ludlow-Partridge | WMA | 3 | 98 | Single-transformer reliability risk
Chester-Worthington-Blandford | WMA | 1 | 75 | 200-mi feeders, reliability
Whately-Deerfield-Hatfield | WMA | 1 |  | DER queue, agricultural/commercial growth
TOTAL

## README
Eversource ESMP Project Pipeline — Extracted from DPU 24-10
Source: | NSTAR Electric Company d/b/a Eversource Energy, Electric Sector Modernization Plan, January 2024 (Exhibit ES-ESMP-1)
Filing: | Massachusetts DPU Docket 24-10
Length: | 699 pages
Sections covered:
Sec 4.3-4.6 — Current state of distribution system per sub-region
Sec 6.5-6.8 — Five- and ten-year planning solutions per sub-region (PRIMARY)
Sec 7.0 — Five-year ESMP investment summary
Sec 7.3 — Execution risks: siting, permitting, supply chain, workforce
Sub-regions:
EMA-North Metro Boston — Boston, Cambridge, Somerville, Chelsea, Brookline, Milton
EMA-North Metro West — 35 communities Metro West & North Shore
EMA-South / SEMA — Cape Cod, South Coast, including New Bedford area
WMA — Western Massachusetts (former WMECO territory)
Why this matters for the permitting platform:
1. This is a leaked customer wishlist — every project here needs siting + permitting.
2. Sec 7.3 explicitly names siting/permitting as #1 execution risk.
3. CEISP (Commission on Clean Energy Infrastructure Siting and Permitting) is making
recommendations on permitting reform — track this.
4. Cross-reference each project location against MassGIS BioMap (Core Habitat,
Critical Natural Landscape) and NHESP Priority/Estimated Habitat for habitat-risk scoring.
Notes on data quality:
- ISD = In-Service Date. For 2030-2034 projects, dates are approximate.
- 'MW Added' = firm capacity addition reported in ESMP. Some upgrades have no clean MW figure.
- Page numbers refer to PDF page in ESMP exhibit.
- Some project IDs are non-numeric where ESMP refers to CIP filings (e.g., 22-47, EFT, WD-CIP).

## Sub-Region Summary
Sub-Region | Projects 2025-2029 | Projects 2030-2034 | Total Projects | Total MW Added
EMA-North Metro Boston
EMA-North Metro West
EMA-South
WMA
TOTAL